## Slide 1
www.sinexcel.us
PWS1 series
PWS1-125M-EX/PWS1-125M-EX-R
PWS1-135M-EX/PWS1-135M-EX-R
Features
PCS integrated with HV Box,system cost reduction
-R version does not integrate the HV box
Wide voltage range of 600~1000Vdc
Compatible with air/liquid-cooling BESS
Multiple mounting methods
Flexible Configuration
High Efficiency & Stability
Extensive Use
Safety & Compatibility
Third-generation semiconductor, silicon carbide
Modular design, easy to install and maintain
Multi-branch battery access cluster management improved battery utilization
Nominal Power Efficiency of 98%
System online rate of 99%
System utilization rate of 99%
Four-quadrant active and reactive regulation
Supports constant power, constant voltage and limit‌‌ing current control
3P4W output for on-grid and off-grid application
Power response speed < 30ms
Compatible with various BMS and EMS
1/21/2026
Notes: Click to add text

## Slide 2
Specification
www.sinexcel.us
1/21/2026
Model | PWS1-125M-EX | PWS1-125M-EX-R | PWS1-135M-EX | PWS1-135M-EX-R
Utility-interactive Mode |  |  |  | 
Nominal Power | 125kW | 125kW | 135kW | 135kW
AC Voltage | 400 (340~460) Vac |  |  | 
DC Voltage Range | 600V~1000V |  |  | 
Voltage for DC Aux port | 600V~1000V |  |  | 
DC Voltage @full load | 665~1000V | 665~1000V | 720~1000V | 720~1000V
Rated Output Power (VA) for AC output port | 125kVA | 125kVA | 135kVA | 135kVA
Rated Output Current (A) for AC output port | 181Aac (125M), 195Aac (135M) |  |  | 
Max DC Current | 193A |  |  | 
AC Connection | 3P4W |  |  | 
AC Frequency | 50±5Hz |  |  | 
THDI | ≤ 3% |  |  | 
Voltage Ripple Coefficient | ≤ 1% |  |  | 
AC PF | -0.8~-1,0.8~1 |  |  | 
Current Overload | 1.1 times long-term |  |  | 
Stand-alone Mode |  |  |  | 
Nominal Power | 125kW | 125kW | 135kW | 135kW
AC Voltage | 400 (340~460) Vac |  |  | 
DC Voltage Range | 600V~1000V |  |  | 
Voltage for DC Aux port | 600V~1000V |  |  | 
DC Voltage @full load | 665~1000V | 665~1000V | 720~1000V | 720~1000V
Max DC Current | 193A |  |  | 
AC Connection | 3P4W |  |  | 
AC Frequency | 50±5Hz |  |  | 
AC PF | -1~-0.3,0.3~1 |  |  | 
Current Overload | 1.1 times long-term, 1.2 times for 1 minute |  |  | 
Aux Port Parameters |  |  |  | 
Rated current for DC Aux port | 10Adc max |  |  | 
Rated Output Power (VA) for AC Aux port | 4.6kVA |  |  | 
Rated Output Current (A) for AC Aux port | 20Ac |  |  | 
Voltage (range) for AC Aux port | 340~460VAc |  |  | 
Frequency (range) for AC Aux port | 45~55Hz |  |  | 
Power factor range for AC Aux port | -1~-0.8, 0.8~1 |  |  | 
System Parameters |  |  |  | 
Nominal Power Efficiency | ≥98% |  |  | 
Dimensions (W*H*D) | 720*265*960mm |  |  | 

## Slide 3
Specification
Noise | ≤75 dB
Weight | ≤115kg
Enclosure | IP66 C5
Operation Temperature | -40℃~ 60℃ ( ≥ 55℃ derating)
Type of the compatible battery (Chemistry) | Lead-acid/LPF/Liquid-flow/Lithium battery/Super capacitor
Cooling | Intelligent air cooling
Operation Humidity | 0~100% (no condensation)
Operation Altitude | 3000 m ( > 3000 m derating)
Communication | 
Communication | RS 485, Ethernet, CAN
Communication Protocol | Modbus TCP/RTU, IEC 104, CAN 2.0
BMS Access | Support
Inverter topology | non‑isolated
1/21/2026
Made in China
Notes: Click to add text